Description

The RTU8171 Keygen provides the Siemens S7-214/224 PLC compatibility with a variety of SCADA and Host CPU systems via radio, modem or general EIA232 interfaces.

Following Materials are supplied with the RTU8171 package:

- RTU8171 Keygen.

- The CDR912-7 cable to connect the 8171 to the S7-214/224 PLC.

- EPROM w/ Modbus Protocol (only with RTU8171-m14).

- RTU Setup Utility Software on a 3.5" diskette.

The user will supply the following materials.

- Siemens S7-214/224 PLC.

- IBM or compatible PC with 3.5" floppy drive.

- A cable connecting the RTU8171 to the appropriate media.

- An available COM1: port on the PC.

RTU8171 Keygen Installation

Jumper Settings

1. EIA232 DTE-DCE (Jumper E1 & 2)

1-2, 3-4		DTE  (Radio, Modem)

1-3, 2-4		DCE  (IBM-PC)

Setting the baud rate

Hardware modifications

Jumper E4.

  - 4800 / 9600 baud. (Factory default)

  - 1200 / 2400 baud.

Modbus protocol modifications

- Up-load memory contents of PLC using the MicroDOS or MicroWIN.

- Edit the following line of code in SBR63:

movb 16#8,smb30	9600 baud	 (Factory default)

Change code to reflect desired baud rate.

movb 16#14,smb30	1200 baud

movb 16#10,smb30	2400 baud

movb 16#C,smb30	4800 baud

Returned Message Delay

movb   +20,vb1338 to movb +50,vb1338

- From the file menu Project/File, download memory to the PLC.

- From the CPU/PLC menu copy program to memory cartridge.

Connectors and wiring

There are two connections on the RTU8171, J1 is the PLC port and J3 is the EIA232 port. J3 is factory set for DTE devices. Table 1 shows the pin-outs of these two connectors.

Table 1: RTU8171 J1 and J3 Pin-outs

| J1 PLC | J3 Line |
| --- | --- |
| Pin | Desc | Pin | DTE | DCE |
| 1 | + 24 Vdc | 1 | RTS | CTS |
| 2 | N/A | 2 | TxD | RxD |
| 3 | TxD/RxD+ | 3 | Gnd | Gnd |
| 4 | TxD/RxD- | 4 | Gnd | Gnd |
| 5 | N/A | 5 | RxD | TxD |
| 6 | + 24 Vdc Rtn | 6 | CTS | RTS |

Connection to an IBM-PC requires an available COM1: port. Use an RJ12 to DE9s adapter cable (CDR912-I) to make this connection. Figure 1 shows the pinout of the CDR912-I cable.

Figure 1 CDR912-I pinout

The RTU8171 connects to the S7-214/224 via the CDR912-7 Cable. Insert the modular phone plug into the PLC port of the RTU8171. Connect the other end of the cable to Port 0 on the PLC. Next, insert the EPROM module into the EPROM slot. Connect the CDR912-7 cable between the RTU8171 and the COM 1 serial port of an IBM-PC. Figure 2 shows the typical installation with an IBM-PC.

Note - This installation refers to a typical hook-up to an IBM-PC. This installation should be used for test purposes before any modem's or radios are installed.

Figure 2 RTU8171 to IBM-PC Installation

Software Installation and Start-up

The “RTU Setup Utility” software may be installed on the hard drive or may run from the floppy drive. To install the software on your hard drive follow the directions below.

Hard Disk Installation

- Insert the 3.5" floppy containing software into drive A.

- Type "a:\install a: c:" to install the software.

- After the installation type "cd c:\MODRTU" to select the software directory.

- Type "modrtu.exe" to run the software program.

- Type the number of the RTU when prompted and press [Return]. default setting is 1.

- The software will search for the RTU.

- Once the RTU is found the RTU type and baud rate will display in the lower right hand corner.

S7-214 Start-up

The following procedure provides the information required to load the Modbus protocol into the S7-214/224 PLC internal memory and start up the PLC. Install the memory cartridge (EPROM) into the memory cartridge receptacle on the PLC. Cycle the power to the PLC. The Modbus protocol is now loaded into the PLCs internal memory. The PLC is now ready to communicate under its default settings.

Quick Start (Do the following before connecting to a radio)

This procedure will provide you with step-by-step instructions on polling the PLC with function code 3: Read Holding Registers. The keygen must be configured for EIA232 DCE (see the jumper settings section in this documentation). This procedure will verify that the PLC is communicating.

- If you have already installed the software on to your hard drive type "modrtu.exe", if not insert the software disk into the floppy drive, access the drive and type "modrtu.exe".

- Enter a "1" at the RTU number prompt. The software will then search for the PLC and connect at the appropriate baud rate. Once connected the software will display "baud xxxx 214RTU" in the lower right corner.

- From the main menu press [F1].

- At the function window press [F3] for Read Holding Registers.

- POLL NUMBER? 				Type "1" press [Return].

- RTU NUMBER? 				Type "1" press [Return].

- STARTING HOLDING REGISTER? 		Type "1" press [Return].

- NUMBER OF HOLDING REGISTERS TO READ? 	Type "9" press [Return].

- Press [F2] to poll and display the data. The holding register response window will then display.

We have now verified that the PLC is communicating through the RTU8171.

Users Programs

User programs are called from CALL 10 (see instructions below). Use the typical installation to an IBM-PC for testing user programs. Refer to the RTU8171 Keygen Installation section for this installation. After programs are tested modems or radios can be installed.

Instructions for calling user programs

- Up-load memory contents of the S7-214/224 using MicroDOS or MicroWIN programming tools.

- Create subroutine 10, for your user program.

- Use CALL 10 for your user program. (See the example program below)

NETWORK 1

LD     SM0.1

CALL   63

NETWORK 2

LD     SM0.7

=      SM30.0

NETWORK 3

LD     V1343.1

=      SM130.0

(

NETWORK 8

LD     SM0.0

CALL   10 	//user subroutine

Starting your Ladders application from within the Modbus Protocol.

- Insert Modbus prom module into the S7-214/224 and power up the unit. Turn mode switch on PLC to the stop position.

- Go on-line using Step 7 Micro/DOS editor and enter the PLC Utilities menu. Go to the program screen and create a backup file of the original program by uploading all the memory contents from the PLC and saving them to a file. Repeat the same procedure to create a different file for your working copy that you will be editing to create your own application prom.

- Go to the Off-line editing mode and edit the file you just created. Edit in the STL mode and insert your CALL subroutine on line CALL10. (See example program on the following page)

Example Program

NETWORK 1

LD     SM0.1

CALL   63

NETWORK 2

LD     SM0.7

=      SM30.0

NETWORK 3

LD     V1343.1

=      SM130.0

(

NETWORK 8

LD     SM0.0

CALL   10 //	enter block here

- Enter the Ladders editing mode use an SBR box function on rung 2 to create your application. Disregard the ILLEGAL NETWORK error message on rung 1. Use RET function on the last rung of your application program to end your subroutine.

Micro-DOS program example

- Save your work when finished and copy the contents of your file to the PLC and then to the memory module once your program has been verified.

Paging and Dial-out Applications

Consult Factory

Siemens Step-7 Support

Table 2: Step-7 Support

| Function | Data Byte | Default |
| --- | --- | --- |
| Station Number* | VB1282 | 1 |
| RTU Type | VB1283 | 3 |
| Baud Rate** | smb30 | 8 (9600 baud) |
| Delays | VB1338 | 20 |
| Delays | VB1339 | 20 |

* The RTU Station number range is from 1 to 254 decimal

** Baud Rates supported for the RTU8171 are 300, 600, 1200, 2400, 4800, and 9600

Modbus Addressing

Table 3: Standard Modbus Addressing

| Discrete Output | Discrete Input |
| --- | --- |
| Modbus | S7 | Modbus | S7 |
| 0,001 | Q0.0 | 10,001 | I0.0 |
| 0,002 | Q0.1 | 10,002 | I0.1 |
| 0,003 | Q0.2 | 10,003 | I0.2 |
| 0,004 | Q0.3 | 10,004 | I0.3 |
| 0,005 | Q0.4 | 10,005 | I0.4 |
| 0,006 | Q0.5 | 10,006 | I0.5 |
| 0,007 | Q0.6 | 10,007 | I0.6 |
| 0,008 | Q0.7 | 10,008 | I0.7 |
| 0,009 | Q1.0 | 10,009 | I1.0 |
| 0,010 | Q1.1 | 10,010 | I1.1 |
|  | 10,011 | I1.2 |
|  | 10,012 | I1.3 |
|  | 10,013 | I1.4 |
|  | 10,014 | I1.5 |

Table 4: S7-214 Packed I/O Addressing

| Packed I/O |
| --- |
| Modbus | S7 | V-Mem |
| 40001 | Status | 1024 |
| 40002 | IW0* | 1026 |
| 40003 | IW2 | 1028 |
| 40004 | IW4 | 1030 |
| 40005 | IW6 | 1032 |
| 40006 | AIW0** | 1034 |
| 40007 | AIW2** | 1036 |
| 40008 | AIW4** | 1038 |
| 40009 | AIW6 | 1040 |
| 40010 | AIW8 | 1042 |
| 40011 | AIW10 | 1044 |
| 40012 | AIW12 | 1046 |
| 40013 | AIW14 | 1048 |
| 40014 | AIW16 | 1050 |
| 40015 | AIW18 | 1052 |
| 40016 | AIW20 | 1054 |
| 40017 | AIW22 | 1056 |
| 40018 | AIW24 | 1058 |
| 40019 | AIW26 | 1060 |
| 40020 | AIW28 | 1062 |
| 40021 | AIW30 | 1064 |
| 40022 | QW0* | 1066 |
| 40023 | QW2 | 1068 |
| 40024 | QW4 | 1070 |
| 40025 | QW6 | 1072 |
| 40026 | AQW2** | 1074 |
| 40027 | AQW4 | 1076 |
| 40028 | AQW6 | 1078 |
| 40029 | AQW8 | 1080 |
| 40030 | AQW10 | 1082 |
| 40031 | AQW12 | 1084 |
| 40032 | AQW14 | 1086 |
| 40033 | AQW16 | 1088 |
| 40034 | AQW18 | 1090 |
| 40035 | AQW20 | 1092 |
| 40036 | User | 1094 |
|  | ¦ |  |
| 40128 | User | 1278 |

* Onboard S7-214/224 I/O

** First EM235 expansion module

Memory Map

Table 5: RTU8171m14/m24 Memory Map

| V0 |  |
| --- | --- |
| thru | CRC Table |
| V512 |  |
| thru | User Memory |
| V1024 |  |
| thru | Packed I/O Holding Registers |
| V1094 |  |
| thru | Holding Registers or User Memory |
| V1279 |  |
| thru | RESERVED |
| V1344 |  |
| thru | User Memory |
| V2014 |  |
| thru | RESERVED |
| V2026 |  |
| thru | User Memory |
| V2906 |  |
| thru | RESERVED |
| V3072 |  |
| thru | Transmit / Receive Buffer |
| V3327 |  |
| thru | RESERVED |
| V4095 |  |

Cable Diagrams

CDR912-7 – Connects the RTU8171 to the PLC.

CDR912-i – Connects the RTU8171 to an IBM-PC serial port (COM 1), 9 pin D-sub, female.

CDR912-r – Connects the RTU8171 to a Radio, 9 pin D-sub, male.

CDR2512-r – Connects the RTU8171 to a Radio, 25 pin D-sub, male.

Ordering Information

RTU8171-m14	S7-214 Keygen Kit, includes RTU8171, modbus protocol on EPROM, RTU Setup Utility software, CDR912-7 cable.

RTU8171-m24	S7-224 Keygen Kit, includes RTU8171, modbus protocol on EPROM, RTU Setup Utility software, CDR912-7 cable.

Spare Parts

S7-EE14MB		S7-214 EPROM with modbus protocol

S7-EE24MB		S7-224 EPROM with modbus protocol

SW-81RSU		RTU Setup Utility software

Cables

CDR912-7			RTU8171 to PLC cable.

CDR912-i			RTU8171 to IBM-PC serial port cable, 9 pin D-sub, female.

CDR912-r			RTU8171 to Radio cable, 9 pin D-sub, male.

CDR2515-r		RTU8171 to Radio cable, 25 pin D-sub, male.

All trademarks acknowledged.

Polybus International is not responsible for any errors or omissions in this documentation.

Polybus International reserves the right to change specifications without notice.

Polybus International, Inc.

1258-H Quarry Lane

Pleasanton, CA 94566

Tel: (925) 426-4815

Fax: (925) 484-5469

Web- http://www.rtu.com