Description

The RTU8175 Bell202 modem provides the Siemens S7-214/224 PLC compatibility with a variety of SCADA and Host CPU systems via radio, lease line, audio or general EIA232 interfaces.

Following Materials are supplied with the RTU8175 package:

- RTU8175 Bell202 Modem.

- The CDR912-7 cable to connect the 8175 to the S7-214/224 PLC.

- EPROM with Modbus Protocol (only with RTU8175-m14).

- “RTU Setup Utility” Software on a 3.5" diskette.

The user will supply the following materials.

- Siemens S7-214 PLC.

- IBM or compatible PC with 3.5" floppy drive.

- A cable connecting the RTU8175 to the appropriate media.

RTU8175 Bell202 Installation

Jumper Settings

E1- Two-wire / four-wire communications

  - Two-wire communications (Factory Setting).

  - Four-wire communications

Adjustments

R22- Transmitter Gain

- Place a 600-Ohm load across TxA- and TxA+.

- Short jumper E4.

- Measure at output.

- Adjust output.

Transmitter gain is adjustable from -20 dB to -3 dB +/- 5%. The factory setting is -9 dB.

Connectors and wiring

There are two connections on the RTU8175, J1 is the PLC port and J3 is the modem port. Table 1 shows the pinouts of these two connectors.

Table 1: RTU8175 J1 and J3 Pin-outs

| J1 PLC | J3 Line |
| --- | --- |
| Pin | Description | Pin | Description |
| 1 | + 24 Vdc | 1 | Earth |
| 2 | N/A | 2 | PTT+ |
| 3 | TxD/RxD+ | 3 | RxA+ |
| 4 | TxD/RxD- | 4 | TxA+ |
| 5 | N/A | 5 | TxA- |
| 6 | + 24 Vdc Rtn | 6 | RxA- |
|  |  | 7 | PTT- |
|  |  | 8 | Common |

The RTU8175 connects to the S7-214 via the CDR912-7 Cable. Insert the modular phone plug side of the cable into the PLC port of the RTU8175. Connect the other side of the cable to the communication port of the S7-214. Next, insert the EPROM module into the EPROM slot on the S7-214. Connect a cable between the RTU8175 and appropriate media. Figure 2 shows a typical installation.

Figure 2: RTU8175 Installation

Software Installation and Start-up

The “RTU Setup Utility” software may be installed on the hard drive or may run from the floppy drive. To install the software on your hard drive follow the directions below.

Hard Disk Installation

- Insert the 3.5" floppy containing software into drive A.

- Type "a:\install a: c:" to install the software.

- After the installation type "cd c:\MODRTU" to select the software directory.

- Type "modrtu.exe" to run the software program.

- Type the number of the RTU when prompted and press [Return]. Default setting is 1.

- The software will search for the RTU.

- Once the RTU is found the RTU type and baud rate will display in the lower right hand corner.

- The RTS/CTS delay will need to be set for some modems. Press [F9] for the configuration menu, then press [F7] for RTS. Follow the instructions on the screen for setting the RTS delay.

S7-214/224 Start-up

The following procedure provides the information required to load the Modbus protocol into the

S7-214/224 internal memory and start up the PLC. Install the EPROM into the memory cartridge receptacle. Cycle the power to the PLC. The Modbus protocol is now loaded into the PLC’s internal memory. The PLC is now ready to communicate under its default settings

Quick Start

This procedure will provide you with step-by-step instructions on polling the PLC with function code 3: Read Holding Registers. This procedure will verify that the PLC is communicating.

- If you have already installed the software on to your hard drive type "MODRTU", if not insert the software disk into the floppy drive, access the drive and type "MODRTU".

- Enter a "1" at the RTU number prompt. The software will then search for the PLC and connect at the appropriate baud rate. Once connected the software will display "baud xxxx xxxRTU" in the lower right corner.

- From the main menu press [F1].

- At the function window press [F3] for Read Holding Registers.

- POLL NUMBER? 				Type "1" press [Return].

- RTU NUMBER? 				Type "1" press [Return].

- STARTING HOLDING REGISTER? 		Type "1" press [Return].

- NUMBER OF HOLDING REGISTERS TO READ? 	Type "9" press [Return].

- Press [F2] to poll and display the data. The holding register response window will then display.

We have now verified that the PLC is communicating through the RTU8175.

Users Programs

User programs are called form line 32 and 33 (see instructions below). Use the hook-up to an IBM-PC for testing user programs. After programs are tested modems or radios can be installed.

Instructions for calling user programs

- Up-load memory contents of S7-214/224 using MicroDOS or MicroWIN programming tools.

- Insert a line after 31 (only 32 and 33 can be used), to call your user program. See the example of the program below.

ADDR	INSTRUCTION

NETWORK1

0  	LD      SM0.1

2  	CALL     K63

5 	LD      SM0.7

7  	=       SM30.0

9  	LD      SM30.0

11  	A        V3069.1

16  	CALL     K61

19  	LD      SM0.0

21  	A        V1343.7

26  	=        V1024.1

31  	CALL     K49

32	User line for calling programs

33	User line for calling programs

34  	MEND

35  	SBR      K49

38  	LD      SM0.0

40  	BMW     IW0         VW1026       K4

50  	SWAP    VW1026

54  	SWAP    VW1028

58  	SWAP    VW1030

Starting your Ladders application from within the Modbus Protocol.

- Insert Modbus prom module into the S7-214/224 and power up the unit. Turn mode switch on PLC to the stop position.

- Go on-line using Step 7 Micro/DOS editor and enter the PLC Utilities menu. Go to the program screen and create a backup file of the original program by uploading all the memory contents from the PLC and saving them to a file. Repeat the same procedure to create a different file for your working copy that you will be editing to create your own application prom.

- Go to the Off-line editing mode and edit the file you just created. Edit in the STL mode and insert your CALL subroutine on line 34. See below

ADDR	INSTRUCTION

NETWORK1

0  	LD      SM0.1

2  	CALL     K63

5 	LD      SM0.7

7  	=       SM30.0

9  	LD      SM30.0

11  	A        V3069.1

16  	CALL     K61

19  	LD      SM0.0

21  	A        V1343.7

26  	=        V1024.1

31  	CALL     K49

34  	CALL     K25     (Enter Your Block Here)

37	MEND

38  	SBR      K49

41  	LD      SM0.0

43  	BMW     IW0         VW1026       K4

53  	SWAP    VW1026

57  	SWAP    VW1028

- Enter the Ladders editing mode use an SBR box function on rung 2 to create your application. Disregard the ILLEGAL NETWORK error message on rung 1. Use RET function on the last rung of your application program to end your subroutine.

- Save your work when finished and copy the contents of your file to the PLC and then to the memory module once your program has been verified.

Paging and Dial-out Applications

Consult Factory

Siemens Step-7 Support

Table 4: Step-7 Support

| Function | Data Byte | Default |
| --- | --- | --- |
| Station Number* | VB1282 | 1 |
| RTU Type | VB1283 | 3 |
| Baud Rate | smb30 | 15 (1200 baud) |
| Delays | VB1338 | 20 |
| Delays | VB1339 | 20 |

* The RTU Station Number range is from 1 to 254 decimal.

Modbus Addressing

Table 2: Standard Modbus Addressing

| Discrete Output | Discrete Input |
| --- | --- |
| Modbus | S7 | Modbus | S7 |
| 0,001 | Q0.0 | 10,001 | I0.0 |
| 0,002 | Q0.1 | 10,002 | I0.1 |
| 0,003 | Q0.2 | 10,003 | I0.2 |
| 0,004 | Q0.3 | 10,004 | I0.3 |
| 0,005 | Q0.4 | 10,005 | I0.4 |
| 0,006 | Q0.5 | 10,006 | I0.5 |
| 0,007 | Q0.6 | 10,007 | I0.6 |
| 0,008 | Q0.7 | 10,008 | I0.7 |
| 0,009 | Q1.0 | 10,009 | I1.0 |
| 0,010 | Q1.1 | 10,010 | I1.1 |
|  |  | 10,011 | I1.2 |
|  |  | 10,012 | I1.3 |
|  |  | 10,013 | I1.4 |
|  |  | 10,014 | I1.5 |

Table 3: S7-214 Packed I/O Addressing

| Packed I/O |
| --- |
| Modbus | S7 | V-Mem |
| 40001 | Status | 1024 |
| 40002 | IW0* | 1026 |
| 40003 | IW2 | 1028 |
| 40004 | IW4 | 1030 |
| 40005 | IW6 | 1032 |
| 40006 | AIW0** | 1034 |
| 40007 | AIW2** | 1036 |
| 40008 | AIW4** | 1038 |
| 40009 | AIW6 | 1040 |
| 40010 | AIW8 | 1042 |
| 40011 | AIW10 | 1044 |
| 40012 | AIW12 | 1046 |
| 40013 | AIW14 | 1048 |
| 40014 | AIW16 | 1050 |
| 40015 | AIW18 | 1052 |
| 40016 | AIW20 | 1054 |
| 40017 | AIW22 | 1056 |
| 40018 | AIW24 | 1058 |
| 40019 | AIW26 | 1060 |
| 40020 | AIW28 | 1062 |
| 40021 | AIW30 | 1064 |
| 40022 | QW0* | 1066 |
| 40023 | QW2 | 1068 |
| 40024 | QW4 | 1070 |
| 40025 | QW6 | 1072 |
| 40026 | AQW2** | 1074 |
| 40027 | AQW4 | 1076 |
| 40028 | AQW6 | 1078 |
| 40029 | AQW8 | 1080 |
| 40030 | AQW10 | 1082 |
| 40031 | AQW12 | 1084 |
| 40032 | AQW14 | 1086 |
| 40033 | AQW16 | 1088 |
| 40034 | AQW18 | 1090 |
| 40035 | AQW20 | 1092 |
| 40036 | User | 1094 |
|  | ¦ |  |
| 40128 | User | 1278 |

* Onboard S7-214 I/O

** First EM235 expansion module

Specifications

Power:				Through S7-214 communication cable

Environmental:

Temperature:		0 - 70 C.

Transmitter:

RTS Delay:		25mS min. key-up

Key-down adjustable to 30S

Key Generation:		Optocoupler open collector

TTL compatible.

Constant carrier:		Continuous carrier in 4-wire mode

Modulator:			Phase coherent FSK

Frequencies:		Bell202 1200	CCITT 600

Mark		1200		1300

Space		2200		1700

Output Level:		Adjustable from 0 to -40db

Filter:			Low pass Fc = 3300Hz

Impedance:		600 Ohms

Operation modes:		2 or 4-wire

Transformer:		Audio BW = 0.3 - 3.0kHz, 600Ohms

Secondary:			Capacitor coupled/gas tube protected

Receiver:

Impedance:		600 Ohms

Input Buffer:		Diode limited, capacitor coupled

Secondary:			Capacitor coupled/gas tube protected

Sensitivity:		-34dB @ 600 Ohms min

Demodulator:		Automatic Gain Control

Low Pass Filter

Group Delay Equalization

Carrier Detection:		On/Off/On delay 25mS max

2.5dB Hysteresis, CD signal

Bias Adjustment:		Continuously adjustable for optimal symmetry

Indicators:

RxD Active:		LED Green

RTS Active:		LED Red

TxD Active:		LED Yellow

Mechanical:

Dimensions:		H6.40" x W1.40" x D3.75"

Connectors:

J1:		RJ45

J2:		RJ12

Mounting:			DIN Rail

Ordering Information

RTU8175-m14	S7-214 Bell202 modem kit, includes: RTU8175, EPROM with modbus protocol, CDR912-7 cable and RTU Setup Utility Software.

RTU8175-m24	S7-224 Bell202 modem kit, includes: RTU8175, EPROM with modbus protocol, CDR912-7 cable and RTU Setup Utility Software.

Spare Parts

S7-EE14MB		S7-214 EPROM with modbus protocol.

S7-EE24MB		S7-224 EPROM with modbus protocol.

SW-81RSU		RTU Setup Utility software.

Cables

CDR912-7			RTU8175 to PLC cable.

All trademarks acknowledged.

Polybus International is not responsible for any errors or omissions in this documentation.

Polybus International reserves the right to change specifications without notice.

Polybus International, Inc.

1258-H Quarry Lane

Pleasanton, CA 94566

Tel: (925) 426-4815

Fax: (925) 484-5469

www.rtu.com